{"text_format":"1","workbook":"xlsx","n_sheets":2,"sheets":["INFO","TLU-01"],"not_rendered":{"charts":1,"images":1,"macros":0,"external_links":0,"defined_names":3,"comments":1,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"INFO","index":0,"n_rows":44,"n_cols":11,"rows_kept":44,"cut":false,"hidden":false,"merged":[[43,0,44,11],[7,0,7,11],[15,0,35,11],[38,0,40,11],[37,0,37,11],[14,0,14,11],[8,0,12,11],[0,10,0,11],[4,0,5,9],[1,10,1,11],[2,10,2,11],[42,0,42,11]]}
[null,null,null,null,null,null,null,null,null,null,"Q199-01"]
[null,null,null,null,null,null,null,null,null,null,"Verze: 4.0"]
[null,null,null,null,null,null,null,null,null,null,"19.01.204"]
[]
["Návrh buňkových tlumičů G / GE / GH"]
[]
[]
["Popis výpočtu:"]
["Výpočtový program je určen pro návrh buňkových tlumičů hluku GREIF instalovaných ve vzduchotechnickém potrubí, nebo stavebně připravených kanálech. Návrh je možné provádět pro všechny standardně vyráběné typy buňkových tlumičů GE / G / GH uspořádané do sestav podle směrnice ITS102-01, kapitoly 5, obrázků a) a b).\nVýpočet je omezen na běžné konstrukční podmínky. V případě složitějších návrhů je nutné tlumič poptat.\nUvedené ceny jsou orientační. Skutečná cena včetně obchodních podmínek bude stanovena na základě nabídky."]
[]
[]
[]
[]
[]
["Nejistota výpočtu:"]
["V září 2018 skončilo přechodné období a vešla v platnost nová, výrazně aktualizovaná norma ČSN EN ISO 9001:2016, která je základním kamenem kvality pro všechny seriózní výrobce. Hlavní změnou je mj. řízení rizik.\n\nZ těchto důvodů uvádíme s útlumem hluku skutečnou odchylku. V oblasti metrologie se nejedná o nic nového, ale u prezentování katalogových hodnot útlumů je to novinka, která od projektanta vyžaduje posouzení instalace v širších souvislostech.\n\nDůvodem je neznalost podmínek, za jakých bude tlumič pracovat. Proto je nutné, aby míru nejistoty posoudil projektant a zohlednil všechny faktory, které mají na útlum hluku vliv. Jsou to zejména neprůzvučnost a tuhost potrubí, ve kterém bude tlumič instalován, provozní podmínky, způsob měření výsledků atd. Je tedy na projektantovi, jakou míru rizika zvolí a odchylku přičte nebo odečte a v jaké velikosti. Námi prezentovaná rozšířená nejistota představuje interval, ve kterém s 95 % pravděpodobností bude ležet měřená hodnota při kombinaci zmíněných místních podmínek.\n\nJe tedy zřejmé, že kvalitní návrh tlumení vyžaduje podrobnou znalost místních podmínek a řízení rizika. Vzhledem k tomu, že jsme již na novou normu recertifikovaní, jsme samozřejmě připraveni tyto rizika minimalizovat a projektantům nabídnout pomocnou ruku při řešení a aplikaci.\n\nV podstatě se nejedná o nic nového, neboť po fyzikální stránce se takto chová každý soubor měření a nezáleží na výrobci nebo způsobu uvádění výsledků. My jako první toto aplikujeme a otevřeně nabízíme pomoc při řešení. Oporou nám jsou interní databáze měřených instalací, při kterých validujeme jednotlivé výsledky a porovnáváme účinnosti jednotlivých řešení."]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Odkaz na projekční katalogy (www.greif.cz):"]
["ITS101-01 - Buňkové tlumiče hluku GE (kašírované provedení)\nITS102-01 - Buňkové tlumiče hluku G (provedení s děrovaným plechem)\nITS103-01 - Buňkové tlumiče hluku GH (hygienické provedení)"]
[]
[]
[]
["Kontakt:"]
["Vaše připomínky na zlepšení, případně objevené chyby můžete posílat na micka@greif.cz.\nV případě, že budete potřebovat pomoc s návrhem tlumičů, kontaktujte naší technickou podporu."]

{"sheet":"TLU-01","index":1,"n_rows":64,"n_cols":48,"rows_kept":64,"cut":false,"hidden":false,"merged":[[41,44,41,47],[44,44,44,47],[60,26,60,28],[0,26,1,38],[3,26,3,28],[3,30,3,32],[19,26,19,28],[23,26,23,28],[36,26,36,28],[35,26,35,28],[35,44,35,47],[42,0,42,11],[42,13,42,24],[18,13,18,24],[35,4,35,10],[36,4,36,10],[26,4,26,10],[27,4,27,10],[28,4,28,10],[29,4,29,10],[30,4,30,10],[29,1,29,2],[30,1,30,2],[31,1,31,2],[32,1,32,2],[19,4,19,10],[33,1,33,2],[38,0,38,11],[25,1,25,2],[23,1,23,2],[24,1,24,2],[26,1,26,2],[36,1,36,2],[32,4,32,10],[33,4,33,10],[21,1,21,2],[34,4,34,10],[34,1,34,2],[35,1,35,2],[22,4,22,10],[23,4,23,10],[31,4,31,10],[22,1,22,2],[27,1,27,2],[28,1,28,2],[24,4,24,10],[25,4,25,10],[0,13,0,24],[6,0,6,11],[7,0,7,11],[12,4,12,9],[19,1,19,2],[10,10,10,11],[11,1,11,2],[4,0,5,11],[9,13,9,16],[9,17,9,23],[9,0,9,2],[9,3,9,11],[14,4,14,10],[15,4,15,10],[17,13,17,24],[2,13,5,14],[20,1,20,2],[11,4,11,10],[13,4,13,10],[12,1,12,2],[16,4,16,10],[17,4,17,10],[18,4,18,10],[17,1,17,2],[18,1,18,2],[13,1,13,2],[14,1,14,2],[15,1,15,2],[16,1,16,2],[20,4,20,10],[1,8,2,11],[62,26,62,28],[63,27,63,28],[63,29,63,42],[6,13,7,14],[6,23,7,24],[44,16,44,18],[44,13,44,15],[45,13,45,21],[45,22,45,24],[44,19,44,21],[44,22,44,24],[43,22,43,24],[43,16,43,18],[43,13,43,15],[43,19,43,21],[3,18,4,19],[6,15,7,22],[2,23,5,24],[3,15,4,15],[3,22,4,22],[2,16,5,17],[2,20,5,21],[21,4,21,10]]}
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Zatlumení zdroje - koncepce výpočtu:",null,null,null,null,null,null,null,null,null,null,null,null,"Data pro návrh buňkových tlumičů"]
[null,null,null,null,null,null,null,null,"Zadejte označení výpočtu"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"ZDROJ\nHLUKU\nLWZ",null,null,"ÚTLUM HLUKU\nTLUMIČEM\nDT, LWT",null,null,null,"ÚTLUM HLUKU\nPOTRUBÍM\nDP",null,null,"VÝSLEDNÝ\nÚTLUM HLUKU\nDC, LWC"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"→",null,null,"→",null,null,null,"→",null,null,null,"Geometrie tlumičů",null,null,null,"Podmínky výběru"]
["Návrh buňkových tlumičů G / GE / GH",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Typ","Šířka","Stěna",null,"Typ","Šířka","Stěna"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"G",200,60,null,{"$f":"CONCATENATE(\"=\",B16)","v":"=G"},{"$f":"B17","v":200},{"$f":"IF(ISERR(DGET(AA5:AC18,\"Stěna\",AE5:AF6)),\"\",DGET(AA5:AC18,\"Stěna\",AE5:AF6))","v":60}]
["Zadejte název projektu",null,null,null,null,null,null,null,null,null,null,null,null,"| ←",null,"CELKOVÝ ÚTLUM HLUKU DC = LWZ - LWC",null,null,null,null,null,null,null,"→ |",null,null,"G",250,80,null,null,"Check:",{"$f":"IF(AG6=\"\",0,1)","v":1}]
["Zadejte název tlumiče",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"G",300,100]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"G",400,100]
["Tlaková ztráta:",null,null,{"$f":"IF(L37=1,\"Zadejte žlutá pole, nebo vepište poznámky…\",\"Zadejte správné hodnoty, nebo vyberte sériově vyráběný element...\")","v":"Zadejte žlutá pole, nebo vepište poznámky…"},null,null,null,null,null,null,null,null,null,"Zatlumení zdroje - výpočet:",null,null,null,"Zadejte tvar hlukového spektra (L = lineární, A = korigované)",null,null,null,null,null,null,"L",null,"G",500,120]
["dpt","=",null,null,null,null,null,null,null,null,{"$f":"IF(OR(B27>25,$L$37=0),\"\",(B30*B23/2*B24^2)*(1+B22))","v":20.705990881639497},null,null,"f","Hz",31.5,63,125,250,500,1000,2000,4000,8000,"A",null,"GE",200,50]
["Q",10000,null,"m3/h","celkový průtok vzduchu tlumičem",null,null,null,null,null,null,{"$f":"IF(B12<=0,0,1)","v":1},null,{"$f":"IF($Y$10=\"L\",\"LWZ-Lin\",IF($Y$10=\"A\",\"LWZ-A\",\"\"))","v":"LWZ-Lin"},"dB",75,90,100,103,99,94,84,78,74,{"$f":"AL27","v":99.888239492271751},null,"GE",250,80]
["a",1000,null,"mm","šířka potrubí (odpovídá násobkům šířky buňky)",null,null,null,null,null,{"$f":"IF($B$17=0,0,IF($B$13/$B$17<1,0,1))","v":1},{"$f":"IF($B$17=0,0,IF($B$13/$B$17=ROUND($B$13/$B$17,0),1,0))","v":1},null,"DT","dB",{"$f":"C45","v":6},6,9,15,26,40,35,30,19,"-",null,"GE",300,100]
["b",1000,null,"mm","výška potrubí (skladem v násobcích 500 mm)",null,null,null,null,null,null,{"$f":"IF(B14<=0,0,1)","v":1},null,{"$f":"IF($Y$10=\"L\",\"LWT-Lin\",IF($Y$10=\"A\",\"LWT-A\",\"\"))","v":"LWT-Lin"},"dB",{"$f":"IF($L$37=0,\"\",IF($Y$10=\"L\",AC29,IF($Y$10=\"A\",AC30,\"\")))","v":47.62756288772281},{"$f":"IF($L$37=0,\"\",IF($Y$10=\"L\",AD29,IF($Y$10=\"A\",AD30,\"\")))","v":41.906901466005564},36.865943591304529,32.656284134383071,28.400206491936679,23.236738552408895,17.487303078054211,11.539185480852787,5.5370234065750026,{"$f":"IF($L$37=0,\"\",$AL$30)","v":30.228826130416952},null,"GH",200,60]
["L",1000,null,"mm","délka tlumiče (1000, 1500 nebo 2000), atypy na vyžádání",null,null,null,null,null,null,{"$f":"IF(OR(B15=1000,B15=1500,B15=2000),1,0)","v":1},null,"DP","dB",0,0,0,0,0,0,0,0,0,"-",null,"GH",250,80]
["typ","G",null,"-","zadejte typ tlumiče \"G\", \"GE\" nebo \"GH\"",null,null,null,null,null,null,{"$f":"IF(OR(B16=\"G\",B16=\"GE\",B16=\"GH\"),1,0)","v":1},null,{"$f":"IF($Y$10=\"L\",\"LWC-Lin\",IF($Y$10=\"A\",\"LWC-A\",\"\"))","v":"LWC-Lin"},"dB",{"$f":"IF($L$37=0,\"\",IF($Y$10=\"L\",AC32,IF($Y$10=\"A\",AC33,\"\")))","v":69.031547306115485},{"$f":"IF($L$37=0,\"\",IF($Y$10=\"L\",AD32,IF($Y$10=\"A\",AD33,\"\")))","v":84.000268201404481},91.000016764006958,88.0000126885528,73.000150590449962,54.003641464501221,49.003064512410511,48.000980965672618,55.000049145549433,{"$f":"IF($L$37=0,\"\",$AL$33)","v":81.100324126050964},null,"GH",300,100]
["š",200,null,"mm","šířka buňky (200, 250, 300, 400, 500) - zpravidla kratší strana elementu",null,"(volte rozměry: 200, 250, 400 a 500)",null,null,null,null,{"$f":"IF(OR(B17=200,B17=250,B17=300,B17=400,B17=500),1,0)","v":1},null,"DC","dB",{"$f":"IF($L$37=0,\"\",AC34)","v":5.9684526938845153},{"$f":"IF($L$37=0,\"\",AD34)","v":5.9997317985955192},8.9999832359930423,14.9999873114472,25.999849409550038,39.996358535498779,34.996935487589489,29.999019034327382,18.999950854450567,{"$f":"IF(OR($L$37=0,$Y$16=\"<20\",$Y$12=\"<20\"),\"\",$Y$12-$Y$16)","v":18.787915366220787},null,"GH",400,100]
["dz1",0.1,null,"-","bez náběhu dz1=1, s náběhem dz1=0,1",null,null,null,null,null,null,{"$f":"IF(OR(B18=1,B18=0.1),1,0)","v":1},null,{"$f":"IF(B17=B13,\"Jeden element v potrubí nefunguje jako tlumič, ale jako obklad potrubí - snížený útlum na cca 50%\",\"\")","v":""},null,null,null,null,null,null,null,null,null,null,null,null,"GH",500,120]
["dz2",0.7,null,"-","bez výběhu dz2=1, s výběhem dz2=0,7",null,null,null,null,null,null,{"$f":"IF(OR(B19=1,B19=0.7),1,0)","v":1},null,"Graf - [dB / Hz]:"]
["t",20,null,"°C","teplota vzduchu (-50 až 200°C)",null,null,null,null,null,null,{"$f":"IF(OR(B20<-50,B20>200),0,1)","v":1},null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korekční křivka"]
["p",101325,null,"Pa","statický tlak v potrubí (98000 až 110000 Pa)",null,null,null,null,null,null,{"$f":"IF(OR(B21<98000,B21>110000),0,1)","v":1},null,null,null,null,null,null,null,null,null,null,null,null,null,null,"f","Hz",31.5,63,125,250,500,1000,2000,4000,8000]
["res",0.2,null,"%","rezerva na místní podmínky",null,null,null,null,null,null,{"$f":"IF(B22<0,0,1)","v":1},null,null,null,null,null,null,null,null,null,null,null,null,null,null,"A","dB",-39.4,-26.2,-16.100000000000001,-8.6,-3.2,0,1.2,1,-1.1000000000000001]
["ro",{"$f":"IF($L$37=0,\"\",$B$21/(287.15*(273.15+$B$20)))","v":1.2036989821185216},null,"kg/m3","hustota vzduchu"]
["w",{"$f":"IF($L$37=0,\"\",$B$12/3600/($B$13*$B$14/1000000))","v":2.7777777777777777},null,"m/s","rychlost proudění vzduchu v profilu a x b",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hladiny hluku"]
["n",{"$f":"IF(OR($L$37=0,$B$17=0),\"\",$B$13/$B$17)","v":5},null,"ks","počet buněk v řadě vedle sebe (= a/š)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"f","Hz",31.5,63,125,250,500,1000,2000,4000,8000,"SUM"]
["s",{"$f":"IF($L$37=0,\"\",$B$17-2*$AG$6)","v":80},null,"mm","průtočná mezera v buňce",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"LWZ-Lin","dB",{"$f":"IF($Y$10=\"L\",P12,IF($Y$10=\"A\",IF((P12-AC22)<0,0,P12-AC22)))","v":75},{"$f":"IF($Y$10=\"L\",Q12,IF($Y$10=\"A\",IF((Q12-AD22)<0,0,Q12-AD22)))","v":90},100,103,99,94,84,78,74,{"$f":"IF(10*LOG10((10^(AC26/10))+(10^(AD26/10))+(10^(AE26/10))+(10^(AF26/10))+(10^(AG26/10))+(10^(AH26/10))+(10^(AI26/10))+(10^(AJ26/10))+(10^(AK26/10)))<20,\"<20\",10*LOG10((10^(AC26/10))+(10^(AD26/10))+(10^(AE26/10))+(10^(AF26/10))+(10^(AG26/10))+(10^(AH26/10))+(10^(AI26/10))+(10^(AJ26/10))+(10^(AK26/10))))","v":106.20956148272913}]
["wi",{"$f":"IF($L$37=0,\"\",($B$12/3600)/($B$26/1000*$B$14/1000*$B$25))","v":6.9444444444444438},null,"m/s",{"$f":"IF(AND(B27>25,L37<>0),\"rychlost proudění překračuje 25 m/s\",\"rychlost proudění uvnitř v tlumiči\")","v":"rychlost proudění uvnitř v tlumiči"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"LWZ-A","dBA",{"$f":"IF($Y$10=\"A\",P12,IF($Y$10=\"L\",IF((P12+AC22)<0,0,P12+AC22)))","v":35.6},{"$f":"IF($Y$10=\"A\",Q12,IF($Y$10=\"L\",IF((Q12+AD22)<0,0,Q12+AD22)))","v":63.8},83.9,94.4,95.8,94,85.2,79,72.900000000000006,{"$f":"IF(10*LOG10((10^(AC27/10))+(10^(AD27/10))+(10^(AE27/10))+(10^(AF27/10))+(10^(AG27/10))+(10^(AH27/10))+(10^(AI27/10))+(10^(AJ27/10))+(10^(AK27/10)))<20,\"<20\",10*LOG10((10^(AC27/10))+(10^(AD27/10))+(10^(AE27/10))+(10^(AF27/10))+(10^(AG27/10))+(10^(AH27/10))+(10^(AI27/10))+(10^(AJ27/10))+(10^(AK27/10))))","v":99.888239492271751}]
["dzs",{"$f":"IF($L$37=0,\"\",(($B$17-$B$26)/$B$26)^2*(0.5*$B$18*($B$26/($B$17-$B$26)+1)+$B$19))","v":1.7625},null,"-","součinitel tlakové ztráty pro náběh a výběh",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"DT","dB",{"$f":"IF(OR($L$37=0,ISERR(DGET(AA37:AQ61,\"31,5\",AS37:AU38))),0,IF(B17=B13,DGET(AA37:AQ61,\"31,5\",AS37:AU38)*0.5,DGET(AA37:AQ61,\"31,5\",AS37:AU38)))","v":6},{"$f":"IF(OR($L$37=0,ISERR(DGET(AA37:AQ61,\"63\",AS37:AU38))),0,IF(B17=B13,DGET(AA37:AQ61,\"63\",AS37:AU38)*0.5,DGET(AA37:AQ61,\"63\",AS37:AU38)))","v":6},{"$f":"IF(OR($L$37=0,ISERR(DGET(AA37:AQ61,\"125\",AS37:AU38))),0,IF(B17=B13,DGET(AA37:AQ61,\"125\",AS37:AU38)*0.5,DGET(AA37:AQ61,\"125\",AS37:AU38)))","v":9},{"$f":"IF(OR($L$37=0,ISERR(DGET(AA37:AQ61,\"250\",AS37:AU38))),0,IF(B17=B13,DGET(AA37:AQ61,\"250\",AS37:AU38)*0.5,DGET(AA37:AQ61,\"250\",AS37:AU38)))","v":15},{"$f":"IF(OR($L$37=0,ISERR(DGET(AA37:AQ61,\"500\",AS37:AU38))),0,IF(B17=B13,DGET(AA37:AQ61,\"500\",AS37:AU38)*0.5,DGET(AA37:AQ61,\"500\",AS37:AU38)))","v":26},{"$f":"IF(OR($L$37=0,ISERR(DGET(AA37:AQ61,\"1000\",AS37:AU38))),0,IF(B17=B13,DGET(AA37:AQ61,\"1000\",AS37:AU38)*0.5,DGET(AA37:AQ61,\"1000\",AS37:AU38)))","v":40},{"$f":"IF(OR($L$37=0,ISERR(DGET(AA37:AQ61,\"2000\",AS37:AU38))),0,IF(B17=B13,DGET(AA37:AQ61,\"2000\",AS37:AU38)*0.5,DGET(AA37:AQ61,\"2000\",AS37:AU38)))","v":35},{"$f":"IF(OR($L$37=0,ISERR(DGET(AA37:AQ61,\"4000\",AS37:AU38))),0,IF(B17=B13,DGET(AA37:AQ61,\"4000\",AS37:AU38)*0.5,DGET(AA37:AQ61,\"4000\",AS37:AU38)))","v":30},{"$f":"IF(OR($L$37=0,ISERR(DGET(AA37:AQ61,\"8000\",AS37:AU38))),0,IF(B17=B13,DGET(AA37:AQ61,\"8000\",AS37:AU38)*0.5,DGET(AA37:AQ61,\"8000\",AS37:AU38)))","v":19},"-"]
["dzf",{"$f":"IF($L$37=0,\"\",0.025*$B$15/$B$26*(1+($B$17-$B$26)/$B$26)^2)","v":1.953125},null,"-","součinitel tlakové ztráty třením v tlumiči",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"LWT-Lin","dB",{"$f":"IF($L$37=0,0,IF($B$37+(10*LOG10($B$21*$B$31*$B$33/$B$36)+60*LOG10($B$32)+10*LOG10(1+($B$31/(2*AC25*$B$34))^2)-10*LOG10(1+(AC25*$B$35/$B$27)^2))<0,0,$B$37+(10*LOG10($B$21*$B$31*$B$33/$B$36)+60*LOG10($B$32)+10*LOG10(1+($B$31/(2*AC25*$B$34))^2)-10*LOG10(1+(AC25*$B$35/$B$27)^2))))","v":47.62756288772281},{"$f":"IF($L$37=0,0,IF($B$37+(10*LOG10($B$21*$B$31*$B$33/$B$36)+60*LOG10($B$32)+10*LOG10(1+($B$31/(2*AD25*$B$34))^2)-10*LOG10(1+(AD25*$B$35/$B$27)^2))<0,0,$B$37+(10*LOG10($B$21*$B$31*$B$33/$B$36)+60*LOG10($B$32)+10*LOG10(1+($B$31/(2*AD25*$B$34))^2)-10*LOG10(1+(AD25*$B$35/$B$27)^2))))","v":41.906901466005564},36.865943591304529,32.656284134383071,28.400206491936679,23.236738552408895,17.487303078054211,11.539185480852787,5.5370234065750026,{"$f":"IF(10*LOG10((10^(AC29/10))+(10^(AD29/10))+(10^(AE29/10))+(10^(AF29/10))+(10^(AG29/10))+(10^(AH29/10))+(10^(AI29/10))+(10^(AJ29/10))+(10^(AK29/10)))<20,\"<20\",10*LOG10((10^(AC29/10))+(10^(AD29/10))+(10^(AE29/10))+(10^(AF29/10))+(10^(AG29/10))+(10^(AH29/10))+(10^(AI29/10))+(10^(AJ29/10))+(10^(AK29/10))))","v":49.090347787745856}]
["dzc",{"$f":"IF($L$37=0,\"\",$B$28+$B$29)","v":3.7156250000000002},null,"-","celkový součinitel tlakové ztráty tlumiče (dzs+dzf)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"LWT-A","dBA",{"$f":"IF($L$37=0,0,IF((AC29+AC22)<0,0,AC29+AC22))","v":8.2275628877228115},{"$f":"IF($L$37=0,0,IF((AD29+AD22)<0,0,AD29+AD22))","v":15.706901466005565},20.765943591304527,24.05628413438307,25.200206491936679,23.236738552408895,18.68730307805421,12.539185480852787,4.4370234065750029,{"$f":"IF(10*LOG10((10^(AC30/10))+(10^(AD30/10))+(10^(AE30/10))+(10^(AF30/10))+(10^(AG30/10))+(10^(AH30/10))+(10^(AI30/10))+(10^(AJ30/10))+(10^(AK30/10)))<20,\"<20\",10*LOG10((10^(AC30/10))+(10^(AD30/10))+(10^(AE30/10))+(10^(AF30/10))+(10^(AG30/10))+(10^(AH30/10))+(10^(AI30/10))+(10^(AJ30/10))+(10^(AK30/10))))","v":30.228826130416952}]
["c",{"$f":"IF($L$37=0,\"\",(1.4*287.15*(273.15+$B$20))^0.5)","v":343.29175856696583},null,"m/s","rychlost zvuku ve vzduchu při teplotě t",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"DP","dB",{"$f":"P15","v":0},{"$f":"Q15","v":0},0,0,0,0,0,0,0,"-"]
["Ma",{"$f":"IF($L$37=0,\"\",$B$27/$B$31)","v":2.0228986776243255E-2},null,"-","Machovo číslo",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"LWC-Lin","dB",{"$f":"IF($L$37=0,0,IF(10*LOG10(10^((AC26-AC28-AC31)/10)+10^(AC29/10))<0,0,10*LOG10(10^((AC26-AC28-AC31)/10)+10^(AC29/10))))","v":69.031547306115485},{"$f":"IF($L$37=0,0,IF(10*LOG10(10^((AD26-AD28-AD31)/10)+10^(AD29/10))<0,0,10*LOG10(10^((AD26-AD28-AD31)/10)+10^(AD29/10))))","v":84.000268201404481},91.000016764006958,88.0000126885528,73.000150590449962,54.003641464501221,49.003064512410511,48.000980965672618,55.000049145549433,{"$f":"IF(10*LOG10((10^(AC32/10))+(10^(AD32/10))+(10^(AE32/10))+(10^(AF32/10))+(10^(AG32/10))+(10^(AH32/10))+(10^(AI32/10))+(10^(AJ32/10))+(10^(AK32/10)))<20,\"<20\",10*LOG10((10^(AC32/10))+(10^(AD32/10))+(10^(AE32/10))+(10^(AF32/10))+(10^(AG32/10))+(10^(AH32/10))+(10^(AI32/10))+(10^(AJ32/10))+(10^(AK32/10))))","v":93.364113688604846}]
["S",{"$f":"IF($L$37=0,\"\",$B$26*$B$14*$B$25/1000000)","v":0.4},null,"m2","plocha nejmenšího průtočného průřezu buňkového tlumiče",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"LWC-A","dBA",{"$f":"IF($L$37=0,0,IF((AC32+AC22)<0,0,AC32+AC22))","v":29.631547306115486},{"$f":"IF($L$37=0,0,IF((AD32+AD22)<0,0,AD32+AD22))","v":57.800268201404478},74.900016764006949,79.400012688552806,69.80015059044996,54.003641464501221,50.203064512410513,49.000980965672618,53.900049145549431,{"$f":"IF(10*LOG10((10^(AC33/10))+(10^(AD33/10))+(10^(AE33/10))+(10^(AF33/10))+(10^(AG33/10))+(10^(AH33/10))+(10^(AI33/10))+(10^(AJ33/10))+(10^(AK33/10)))<20,\"<20\",10*LOG10((10^(AC33/10))+(10^(AD33/10))+(10^(AE33/10))+(10^(AF33/10))+(10^(AG33/10))+(10^(AH33/10))+(10^(AI33/10))+(10^(AJ33/10))+(10^(AK33/10))))","v":81.100324126050964}]
["H",{"$f":"IF($L$37=0,\"\",IF($B$13>$B$14,$B$13/1000,$B$14/1000))","v":1},null,"m","největší příčný rozměr potrubí",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"DC","dB",{"$f":"IF($L$37=0,0,IF($Y$10=\"L\",AC26-AC32,IF($Y$10=\"A\",AC27-AC33,\"\")))","v":5.9684526938845153},{"$f":"IF($L$37=0,0,IF($Y$10=\"L\",AD26-AD32,IF($Y$10=\"A\",AD27-AD33,\"\")))","v":5.9997317985955192},8.9999832359930423,14.9999873114472,25.999849409550038,39.996358535498779,34.996935487589489,29.999019034327382,18.999950854450567,"-"]
["delta",{"$f":"IF($L$37=0,\"\",0.02)","v":0.02},null,"-","spektrální obsah vysokých kmitočtů"]
["W0",{"$f":"IF($L$37=0,\"\",1)","v":1},null,"W","referenční výkon",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Data katalog",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Podmínky výběru DT"]
["B",{"$f":"IF($L$37=0,\"\",63)","v":63},null,"dB","konstanta tlumiče",null,null,null,null,null,null,{"$f":"L12*L13*L14*L15*L16*L17*L18*L19*L20*L21*L22*AG7*AV39","v":1},null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Označení tlumiče",null,null,"Typ","Šířka","Délka","Váha","Cena",31.5,63,125,250,500,1000,2000,4000,8000,null,"Typ","Šířka","Délka","Váha"]
[null,null,null,null,null,null,null,null,null,null,null,"Výpočet je proveden dle ČSN EN ISO 14163, odhad nepřesnosti ± 10%",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"G200x500x1000",null,null,"G",200,1000,10,1720,6,6,9,15,26,40,35,30,19,null,{"$f":"CONCATENATE(\"=\",B16)","v":"=G"},{"$f":"B17","v":200},{"$f":"IF($B$15=1000,1000,IF($B$15=1500,1500,IF($B$15=2000,2000,0)))","v":1000},{"$f":"IF(ISERR(DGET(AA37:AQ61,\"Váha\",AS37:AU38)),\"\",DGET(AA37:AQ61,\"Váha\",AS37:AU38))","v":10}]
["Vlastní hluk:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"G200x500x1500",null,null,"G",200,1500,15,2685,7,7,12,21,38,43,40,33,26,null,null,null,"Check:",{"$f":"IF(AV38=\"\",0,1)","v":1}]
["f","Hz",31.5,63,125,250,500,1000,2000,4000,8000,"LWT-A",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"G200x500x2000",null,null,"G",200,2000,24,3375,8,9,15,28,43,48,46,40,30]
["LWT-Lin","dB",{"$f":"IF($L$37=0,\"\",AC29)","v":47.62756288772281},{"$f":"IF($L$37=0,\"\",AD29)","v":41.906901466005564},36.865943591304529,32.656284134383071,28.400206491936679,23.236738552408895,17.487303078054211,11.539185480852787,5.5370234065750026,{"$f":"IF($L$37=0,\"\",$AL$30)","v":30.228826130416952},null,null,null,null,null,null,null,null,null,null,null,null,null,null,"G250x500x1000",null,null,"G",250,1000,11,1830,6,7,11,16,29,41,34,26,17]
[null,null,null,null,null,null,null,null,null,null,null,"Výpočet je proveden dle ČSN EN ISO 14163, odhad nepřesnosti ± 3 dB",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"G250x500x1500",null,null,"G",250,1500,17,2900,8,8,15,23,41,43,37,31,23,null,"Ozačení tlumiče"]
["Útlum a váha buňkového tlumiče:",null,null,null,null,null,null,null,null,null,null,null,null,"Závěrečné shrnutí výsledků:",null,null,null,null,null,null,null,null,null,null,null,null,"G250x500x2000",null,null,"G",250,2000,26,3620,9,11,18,28,42,47,43,36,27,null,{"$f":"IF(ISERR(DGET(AA37:AQ61,\"Označení tlumiče\",AS37:AU38)),\"Atypický rozměr\",IF(MOD(B14,500)>0,\"Atypický rozměr\",CONCATENATE(DGET(AA37:AQ61,\"Označení tlumiče\",AS37:AU38),AV43)))","v":"G200x500x1000.1"},null,null,{"$f":"IF(AND(B18=0.1,B19=0.7),\".1\",IF(AND(B18=1,B19=1),\".3\",\".2\"))","v":".1"}]
["f","Hz",31.5,63,125,250,500,1000,2000,4000,8000,"M",null,"Instalační rozměr potrubí",null,null,{"$f":"IF($L$37=0,\"\",CONCATENATE(B13,\" x \",B14,\" - \",B15))","v":"1000 x 1000 - 1000"},null,null,"Počet buňek v tlumiči",null,null,{"$f":"IF(OR($L$37=0,$Q$45=\"Atypický rozměr\"),\"Zašlete poptávku\",($B$13*$B$14*$B$15)/($B$17*500*$B$15))","v":10},null,null,null,"G300x500x2000",null,null,"G",300,2000,31,3870,9,10,18,34,44,50,47,42,30]
["DT","dB",{"$f":"IF(OR($L$37=0,$K$13=0),\"\",AC28)","v":6},{"$f":"IF(OR($L$37=0,$K$13=0),\"\",AD28)","v":6},9,15,26,40,35,30,19,"kg/ks",null,"Označení tlumiče",null,null,{"$f":"IF($L$37=0,\"\",$AS$43)","v":"G200x500x1000.1"},null,null,"Hmotnost bez potrubí",null,null,{"$f":"IF(OR($L$37=0,$Q$45=\"Atypický rozměr\"),\"Zašlete poptávku\",$W$44*$L$46)","v":100},null,null,null,"G400x500x2000",null,null,"G",400,2000,34,4885,8,9,19,28,36,43,35,25,15,null,"Cena tlumiče"]
["2sigR","dB",{"$f":"IF(C45=\"\",\"\",7)","v":7},{"$f":"IF(D45=\"\",\"\",6)","v":6},{"$f":"IF(E45=\"\",\"\",4)","v":4},{"$f":"IF(F45=\"\",\"\",4)","v":4},4,4,4,4,{"$f":"IF(K45=\"\",\"\",7)","v":7},{"$f":"IF($L$37=0,\"\",$AV$38)","v":10},null,"Brutto cena buňkových tlumičů bez potrubí (bez DPH, EXW Uhlířské Janovice)",null,null,null,null,null,null,null,null,{"$f":"IF($W$44=\"Zašlete poptávku\",\"Zašlete poptávku\",$W$44*$AS$46)","v":17200},null,null,null,"G500x500x2000",null,null,"G",500,2000,36,5505,9,11,20,30,34,36,30,22,13,null,{"$f":"IF(AS43=\"Atypický rozměr\",\"\",DGET(AA37:AQ61,\"Cena\",AS37:AU38))","v":1720},"Kč/ks"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GE200x500x1000",null,null,"GE",200,1000,7.3,1265,5,5,8,14,24,40,36,29,20]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GE200x500x1500",null,null,"GE",200,1500,10.8,2095,6,6,11,19,32,42,39,35,24]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GE250x500x1000",null,null,"GE",250,1000,8.6,1360,6,7,11,16,29,45,40,32,23]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GE250x500x1500",null,null,"GE",250,1500,12.8,2340,8,8,15,23,41,46,43,38,28]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GE300x500x1000",null,null,"GE",300,1000,11.8,1440,7,8,12,19,34,46,41,31,20]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GE300x500x1500",null,null,"GE",300,1500,16.5,2580,8,9,17,27,40,49,47,39,22]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GH200x500x1000",null,null,"GH",200,1000,10,1935,6,6,9,15,26,28,24,18,10]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GH200x500x1500",null,null,"GH",200,1500,15,2990,7,7,12,21,30,33,30,20,12]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GH200x500x2000",null,null,"GH",200,2000,24,3790,8,9,15,28,36,40,37,28,20]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GH250x500x1000",null,null,"GH",250,1000,11,2055,6,7,11,16,25,27,23,17,9]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GH250x500x1500",null,null,"GH",250,1500,17,3220,8,8,15,23,30,32,29,21,11]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GH250x500x2000",null,null,"GH",250,2000,26,4035,9,11,18,28,35,38,34,26,17]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GH300x500x2000",null,null,"GH",300,2000,31,4285,9,10,18,32,38,39,37,32,25]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GH400x500x2000",null,null,"GH",400,2000,34,5300,8,9,19,28,36,38,32,25,17]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GH500x500x2000",null,null,"GH",500,2000,36,5940,9,11,20,30,34,36,30,22,13]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Aktualizace SW"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"3.0","2023-03-19",null,"Oprava útlumu 1 buňky na 50%, roztažení poznámek, změna formátování popisků LWZ-Lin, změna tisku na 1 A4 na ležato, aktualizace cen tlumičů."]